## Sheet1
VOLTAGE DROP CALCULATION | [7 empty] | Table 10.1.1.9 Alternating-Current Resistance and Reactance for 600-Volt Cable, 3-Phase, 60 Hz, 75C- Three Single Conductors in Conduit
X (REACTANCE) |  | R (RESISTANCE) | DISTANCE (m) |  | CONSTANT (K) |  | I (ISC) | Conductor Size [mm2 (mm dia)] | Ohms to Neutral per 305 m
0.054 |  | 2 | 50 |  | 2 |  | 13 |  | XL (Reactance) for All wires |  | Alternating-Current Resistance for Uncoated Copper Wires |  |  | Alternating-Current Resistance for Aluminum Wires
X^2 = | 0.002916 | [7 empty] | PVC/ Aluminum Conduits | Steel Conduits | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit
R^2 = | 4 |  |  | CONSTANT (K) |  | 2 (SINGLE PHASE)
r^2 + x^2 = | 4.0029 |  |  |  |  | 1.732 (THREE PHASE)
Z = | 2.0007 | [6 empty] | 2.0(1.6)* | 0.058 | 0.073 | 3.1 | 3.1 | 3.1 | - | - | -
[8 empty] | 3.5(2.0)* | 0.054 | 0.068 | 2 | 2 | 2 | 3.2 | 3.2 | 3.2
[8 empty] | 5.5(2.6)* | 0.05 | 0.063 | 1.2 | 1.2 | 1.2 | 2 | 2 | 2
V Drop | 8.5277 | volts |  |  | V Drop % = | 3.553% |  | 8.0(3.2) | 0.052 | 0.065 | 0.78 | 0.78 | 0.78 | 1.3 | 1.3 | 1.3
[8 empty] | 14 | 0.051 | 0.064 | 0.49 | 0.49 | 0.49 | 0.81 | 0.81 | 0.81
Nominal Voltage | 350 | volts | [5 empty] | 22 | 0.048 | 0.06 | 0.31 | 0.31 | 0.31 | 0.51 | 0.51 | 0.51
Voltage (at the end) = | 341.4723 | volts | [5 empty] | 30 | 0.045 | 0.057 | 0.19 | 0.2 | 0.2 | 0.32 | 0.32 | 0.32
[8 empty] | 38 | 0.046 | 0.057 | 0.15 | 0.16 | 0.16 | 0.25 | 0.26 | 0.25
[8 empty] | 50 | 0.044 | 0.055 | 0.12 | 0.13 | 0.12 | 0.2 | 0.21 | 0.2
[8 empty] | 60 | 0.043 | 0.054 | 0.1 | 0.1 | 0.1 | 0.16 | 0.16 | 0.16
[8 empty] | 80 | 0.042 | 0.052 | 0.077 | 0.082 | 0.079 | 0.13 | 0.13 | 0.13
[8 empty] | 100 | 0.041 | 0.051 | 0.062 | 0.067 | 0.063 | 0.1 | 0.11 | 0.1
[8 empty] | 125 | 0.041 | 0.052 | 0.052 | 0.057 | 0.054 | 0.085 | 0.09 | 0.086
[8 empty] | 150 | 0.041 | 0.051 | 0.044 | 0.049 | 0.045 | 0.071 | 0.076 | 0.072
[8 empty] | 175 | 0.04 | 0.05 | 0.038 | 0.043 | 0.039 | 0.061 | 0.066 | 0.063
[8 empty] | 200 | 0.04 | 0.049 | 0.033 | 0.038 | 0.035 | 0.054 | 0.059 | 0.055
[8 empty] | 250 | 0.039 | 0.048 | 0.027 | 0.032 | 0.029 | 0.043 | 0.048 | 0.045
[8 empty] | 325 | 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038
[8 empty] | 375 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
[8 empty] | 400 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
[8 empty] | 500 | 0.037 | 0.046 | 0.015 | 0.019 | 0.018 | 0.023 | 0.027 | 0.025